## Bus Data
B1
B2
B3
B4
B5
A
B
C
BB

## Line Data
| Length | Upstream Bus | Downstream Bus | Fuse/breaker direction | Disconnector direction | Cable Type | Nr Transformers | Transformer Type
MF | 0 | B1 | B2 | U | N | Line 1 | 0 | 0
S1 | 2 | B2 | B3 | N | D | Line 1 | 0 | 0
S2 | 3 | B3 | B4 | N | D | Line 1 | 0 | 0
S3 | 1 | B4 | B5 | N | D | Line 1 | 0 | 0
L1 | 3 | B2 | A | U | N | Line 2 | 0 | 0
L2 | 2 | B3 | B | U | N | Line 2 | 0 | 0
L3 | 1 | B4 | C | U | N | Line 2 | 0 | 0

## Load Point Data
| Customer type | Load level average [MW] | Load point peak [MW] | Number of customers
A | residential | 0.535 | 0.8668 | 250
B | residential | 0.535 | 0.8668 | 100
C | residential | 0.535 | 0.8668 | 50

## Generation Data
| Lim MW | E cap | Main Feeder
B1 | 0 | 0 | True
BB | 0 | 0 | True
B4 | 3 | 2 | False

## Backup Feeders
| End 1 | End 2 | s
BS | B5 | BB | 1

## Component Data
Component | lambda | r | s
Line 1 | 0.1 | 3 | 0.5
Line 2 | 0.25 | 1 | 0.5

## Weekly Load Factor
Week | Load Factor
1 | 86.2
2 | 90
3 | 87.8
4 | 83.4
5 | 88
6 | 84.1
7 | 83.2
8 | 80.6
9 | 74
10 | 73.7
11 | 71.5
12 | 72.7
13 | 70.4
14 | 75
15 | 72.1
16 | 80
17 | 75.4
18 | 83.7
19 | 87
20 | 88
21 | 85.6
22 | 81.1
23 | 90
24 | 88.7
25 | 89.6
26 | 86.1
27 | 75.5
28 | 81.6
29 | 80.1
30 | 88
31 | 72.2
32 | 77.6
33 | 80
34 | 72.9
35 | 72.6
36 | 70.5
37 | 78
38 | 69.5
39 | 72.4
40 | 72.4
41 | 74.3
42 | 74.4
43 | 80
44 | 88.1
45 | 88.5
46 | 90.9
47 | 94
48 | 89
49 | 94.2
50 | 97
51 | 100
52 | 95.2

## Daily Load Factor
Day of week | Load Factor
1 | 93
2 | 100
3 | 98
4 | 96
5 | 94
6 | 77
7 | 75

## Hourly Load Factor
Hours | Winter Wkdy | Winter Wknd | Summer Wkdy | Summer Wknd | Spring/Fall Wkdy | Spring/Fall Wknd
1 | 67 | 78 | 64 | 74 | 63 | 75
2 | 63 | 72 | 60 | 70 | 62 | 73
3 | 60 | 68 | 58 | 66 | 60 | 69
4 | 59 | 66 | 56 | 65 | 58 | 66
5 | 59 | 64 | 56 | 64 | 59 | 65
6 | 60 | 65 | 58 | 62 | 65 | 65
7 | 74 | 66 | 64 | 62 | 72 | 68
8 | 86 | 70 | 76 | 66 | 85 | 74
9 | 95 | 80 | 87 | 81 | 95 | 83
10 | 96 | 88 | 95 | 86 | 99 | 89
11 | 96 | 90 | 99 | 91 | 100 | 92
12 | 95 | 91 | 100 | 93 | 99 | 94
13 | 95 | 90 | 99 | 93 | 93 | 91
14 | 95 | 88 | 100 | 92 | 92 | 90
15 | 93 | 87 | 100 | 91 | 90 | 90
16 | 94 | 87 | 97 | 91 | 88 | 86
17 | 99 | 91 | 96 | 92 | 90 | 85
18 | 100 | 100 | 96 | 94 | 92 | 88
19 | 100 | 99 | 93 | 95 | 96 | 92
20 | 96 | 97 | 92 | 95 | 98 | 100
21 | 91 | 94 | 92 | 100 | 96 | 97
22 | 83 | 92 | 93 | 93 | 90 | 95
23 | 73 | 87 | 87 | 88 | 80 | 90
24 | 63 | 81 | 72 | 80 | 70 | 85